## Headrace Design
⚡ HEADRACE DESIGN TOOL ⚡ | [8 empty] | GUIDE USER
|  |  | Loss Type | Loss (m) | Head Type | Value (m) | Efficiency | Power (kW) | This Headrace Design Tool is a comprehensive spreadsheet that automatically calculates: |  |  |  | Site Data: B4-B9
BASIC PROJECT INPUTS |  |  | Intake | 0.050968 | Gross Head | 50 | Power @ 75% | 620.0553 | ✅ All energy losses (friction, bends, expansions) |  |  |  | Intake Settings: B12-B13 | Cell | Full Name | Formula/Input | Type | Value
Gross Head (m) | 50 | m | Conveyance | 7.8114 | Total Losses | 7.8624 | Power @ 80% | 661.3923 | ✅ Component sizes (intake, pipe, penstock) |  |  |  | Pipe Parameters: B24-B29 | B4 | Gross Head | User Input (m) | INPUT | 50 m
Discharge (m³/s) | 2 | m³/s |  |  | Net Head | 42.1376 | Power @ 85% | 702.7293 | ✅ Net head availability (power potential) |  |  |  | Channel Parameters: B32-B38 | B5 | Discharge | User Input (m³/s) | INPUT | 2 m³/s
Water Density (kg/m³) | 1000 | kg/m³ | [6 empty] | ✅ Hydraulic power (raw water power) |  |  |  | Penstock Settings: B65-B66 | B6 | Water Density | 1000 (kg/m³) | CONSTANT | 1000
Gravity (m/s²) | 9.81 | m/s² | [6 empty] | ✅ Annual energy generation (revenue projection) |  |  |  |  | B7 | Gravity | 9.81 (m/s²) | CONSTANT | 9.81
Kinematic Viscosity (m²/s) | 1e-06 | m²/s | [6 empty] | ✅ Financial viability (payback period, ROI) |  |  |  |  | B8 | Kinematic Viscosity | 0.000001 (m²/s) | CONSTANT | 1e-06
Bulk Modulus Water (MPa) | 2200 | MPa | [11 empty] | B9 | Bulk Modulus Water | 2200 (MPa) | CONSTANT
[9 empty] | cell | PIPE MODE (B22=0): For pressurized pipe systems |  | Shows pipe calculations (B43-B50)
[9 empty] | B22 | CHANNEL MODE (B22=1): For open channel systems |  | Shows channel calculations (B53-B60)
INTAKE LOSSES & SIZING | [8 empty] | B14 | Entry Type (0=rounded, 1=sharp): B12 = 80 (good balance between flow and cleaning), B13 = 0 (rounded entry is better, less loss)
Trash Rack Open % | 80 | [7 empty] | B33 | Channel Type (0=Rect, 1=Trap) | B32: 0 for simple rectangular, 1 for sloped sides
Entry Type (0=rounded, 1=sharp) | 0 | [7 empty] | AUTO-TOGGLE: System automatically selects the better option so don't edit formular, just edit the input, you'll see changes in output. Don't edi formula!
|  |  | Loss Component | Loss (m) | Component | Size (m) | Efficiency | Energy (MWh)
Intake Diameter (2.0 m/s optimal) | 0.79788 |  | Trash Rack | 0.040775 | Intake Diameter | 0.79788 | Annual Energy @ 75% | 4960.4423 | Input Data & Calculations
Trash Rack Loss | 0.040775 |  | Entry | 0.010194 | Penstock Diameter | 1.0638 | Annual Energy @ 85% | 5621.8346 | (Columns A-B)
Entry Loss | 0.010194 |  | Friction | 6.5768 | Recommended Depth | 0 |  |  | Yellow cells = YOUR INPUTS
TOTAL INTAKE LOSS | 0.050968 |  | 90° Bends | 0.36311 |  |  |  |  | Green cells = AUTOMATIC CALCULATIONS
|  |  | 45° Bends | 0.064552 |  |  |  |  | Colored headers = Section categories
CONVEYANCE LOSSES & SIZING |  |  | Expansion/Contraction Loss | 0.8069 |  |  |  |  | B43 = Pipe Velocity (should be 2-4 m/s)
Conveyance Type (0=Pipe, 1=Channel) | 0 | [7 empty] | B46 = Friction Loss (biggest loss)
B50 = Total Pipe Loss
----PIPE PARAMETERS --- | [8 empty] | B81 = Hydraulic Power (in kW)
Pipe Diameter (m) | 0.8
Pipe Length (m) | 500 | [7 empty] | #Try Filing channel parameters (B32-B38):
Pipe Roughness (m) | 0.0001 | [7 empty] | B33 = 0 (rectangular) or 1 (trapezoidal)
Number of 90° Bends | 3 | [7 empty] | B34 = Channel width (e.g., 2m)
Number of 45° Bends | 2 | [7 empty] | B35 = Channel depth (e.g., 1.5m)
Expansions/Contractions | 2 | [7 empty] | B36 = Side slope (e.g., 1.5 for trapezoid)
B37 = Channel length (e.g., 100m)
--- CHANNEL PARAMETERS --- | [8 empty] | B38 = Manning n (0.015 for concrete)
Channel Type (0=Rect, 1=Trap) | 0 | [7 empty] | B39 = Channel slope (0.002 typical)
Channel Width (m) | 2 | [7 empty] | B62 = Total Conveyance Loss (uses best system)
Channel Depth (m) | 1.5 | [7 empty] | B77 = Total Losses (intake + conveyance)
Side Slope (H:V) | 1.5 | [7 empty] | B78 = NET HEAD (critical number!)
Channel Length (m) | 100 | [7 empty] | B81 = HYDRAULIC POWER (your power potential)
Manning n | 0.015
Channel Slope | 0.002
DO:
[9 empty] | ├─ Save file regularly (Ctrl+S) |  | REMEMBER
PIPE CALCULATIONS | [8 empty] | ├─ Make copies for each scenario (v1.0, v2.0) |  | Key Rules:
Pipe Velocity | 3.9789 | [7 empty] | ├─ Test both pipe AND channel modes |  | 1. Yellow cells = YOU FILL (Inputs)
Reynolds Number | 3183098.8618 | [7 empty] | ├─ Change one parameter at a time |  | 2. Green cells = AUTO-CALCULATE (Formulas)
Friction Factor | 0.013041 | [7 empty] | ├─ Watch how each change affects power |  | 3. DON'T EDIT GREEN CELLS (breaks formulas!)
Friction Loss | 6.5768 | [7 empty] | ├─ Document best scenario |  | 4. B21 AUTO-TOGGLES (B21 = IF B50<B60...)
90° Bend Loss | 0.36311 | [7 empty] | └─ Print results before finalizing |  | 5. B78 IS CRITICAL (Net Head = Everything!)
45° Bend Loss | 0.064552 | [9 empty] | 6. B81 IS POWER (Raw water power)
Expansion/Contraction Loss | 0.8069 | [7 empty] | ❌ DON'T: |  | 7. B74 IS PENSTOCK (Wall thickness to order)
TOTAL PIPE LOSS | 7.8114 | [7 empty] | ├─ Edit green cells (formulas!) |  | 8. B77 IS LOSSES (Where energy goes)
├─ Use unrealistic parameters
CHANNEL CALCULATIONS | [8 empty] | ├─ Forget to fill BOTH pipe AND channel params
Channel Area | 0 | [7 empty] | ├─ Ignore the loss distribution chart
Wetted Perimeter | 0 | [7 empty] | ├─ Use gross head in power calculations
Hydraulic Radius | 0 | [7 empty] | ├─ Accept first calculation (optimize!)
Channel Velocity | 0
Manning Friction Loss | 0
Recommended Depth | 0
Freeboard (min 0.5m) | 0
TOTAL CHANNEL LOSS | 0
TOTAL CONVEYANCE LOSS | 7.8114
PENSTOCK SIZING
Valve Closure Time (s) | 2
Safety Factor | 1.5
Optimal Penstock Diameter | 1.0638
Speed of Sound (a) | 1483.2397
Surge Pressure | 5.9016
Static Pressure | 0.41337
Design Pressure | 6.315
Hoop Stress Thickness | 20.1545
DESIGN WALL THICKNESS | 22.1545
NET HEAD & POWER CALCULATIONS
TOTAL LOSSES | 7.8624
NET HEAD | 42.1376
Head Efficiency % | 84.2753
HYDRAULIC POWER | 826.7404
Power @ 75% | 620.0553
Power @ 80% | 661.3923
Power @ 85% | 702.7293
Annual Energy @ 75% | 4960.4423
Annual Energy @ 85% | 5621.8346